www.proscada.com

PO Box 417						Phone	: +27 12 3482151

Newlands						Fax	: +27 12 3482151

0049							Cellular: +27 82 4596208

South Africa						email	:jon.pio@proscada.com

# “I87” OPC Server IEC 870-5-103 Implementation guidlines

Unfortunately IEC 870-5-103 is a very poorly designed protocol, so some of these concepts are a little strange.

The Analog Address format is:

<Relay Name>:<function type>:<Information object>

The Digital Address format is:

<Relay Name>:<function type>:<Information object>:<bit>

Relay Name 		the name of the protection device, printable characters upto 11 characters long, may not include any of  “:;,  “

Function type	Specifies the type of message, used together with the Information Object to Identify the data.

Information object	Specifies the number of the value.  ***NOTE when configuring the driver poll blocks the address of the start address corresponds to the IEC standard messages.  When entering an address in a OPC client the Position number of the address is increments of 1 from this address.

Example Standard IEC data

RTU1:160:144			Current I

RTU1:160:145			Voltage V

RTU1:160:146			Power

RTU1:160:147			Q factor

RTU1:128:148			Current IL1

RTU1:128:149			Current IL2

RTU1:128:150			Current IL3

RTU1:128:151			Voltage IL1-e

RTU1:128:152			Voltage IL2-e

RTU1:128:153			Voltage IL3-e

RTU1:128:154			Power

RTU1:128:155			Q factor

RTU1:128:155			Frequency

These addresses will return the raw unscaled analog value, the value can be scaled either by the SCADA client OR the OPC server.

To scale the values in the OPC server add the following text to the address

|M103,<lo engineering unit>,<hi engineering unit>,<raw lo:raw hi>,<units optional>

example 1

a Reyrolle Relay scales 0 – 3412 so if the rated range is 100 amps

RTU1:160:144	|M103,0,100.0,0:3412,A

Example 2 Siemens Siprotec

Setup the driver poll blocks as follows:

A Siemens SIPROTEC scales 1.7% to 240% with a raw range of 0-4095 and 100% = 1706

Current 		RTU1:134:137|M103,1.7,100.0,0:1706,%

Frequency		RTU1:134:149|M103,47.0,53.0,0:4095,hz

Example Siemens SIProtec Non compatible data

| Driver OPC Address | Siemens Measurand | Name | Descrption |
| --- | --- | --- | --- |
| RTU1:134:137¦M103,1.7,100.0,0:1706,% | 601 | Ia | (Ia =) Measurement 134 137 No 3 1 CFC CD DD |
| RTU1:134:138¦M103,1.7,100.0,0:1706,% | 602 | Ib | (Ib =) Measurement 134 137 No 3 2 CFC CD DD |
| RTU1:134:139¦M103,1.7,100.0,0:1706,% | 603 | Ic | (Ic =) Measurement 134 137 No 9 3 CFC CD DD |
| RTU1:134:140¦M103,1.7,100.0,0:1706,% | 604 | In | (In =) Measurement 134 137 No 9 4 CFC CD DD |
| RTU1:134:141¦M103,1.7,100.0,0:1706,% | 621 | Va | (Va =) Measurement 134 137 No 9 5 CFC CD DD |
| RTU1:134:142¦M103,1.7,100.0,0:1706,% | 622 | Vb | (Vb =) Measurement 134 137 No 9 6 CFC CD DD |
| RTU1:134:143¦M103,1.7,100.0,0:1706,% | 623 | Vc | (Vc =) Measurement 134 137 No 9 7 CFC CD DD |
| RTU1:134:144¦M103,1.7,100.0,0:1706,% | 624 | Va-b | (Va-b=) Measurement 134 137 No 9 8 CFC CD |
| RTU1:134:145¦M103,1.7,100.0,0:1706,% | 625 | Vb-c | (Vb-c=) Measurement 134 137 No 9 9 CFC CD |
| RTU1:134:146¦M103,1.7,100.0,0:1706,% | 626 | Vc-a | (Vc-a=) Measurement 134 137 No 9 10 CFC CD |
| RTU1:134:147¦M103,1.7,100.0,0:1706,% | 641 | P | (active power) (P =) Measurement 134 137 No 9 11 CFC |
| RTU1:134:148¦M103,1.7,100.0,0:1706,% | 642 | Q | (reactive power) (Q =) Measurement 134 137 No 9 12 CF |
| RTU1:134:149¦M103,1.7,100.0,0:1706,% | 644 | Frequency | (Freq=) Measurement 134 137 No 9 13 C |
| RTU1:134:150¦M103,1.7,100.0,0:1706,% | 901 | Power Factor | (PF =) 134 137 No 9 14 |
| RTU1:134:151¦M103,1.7,100.0,0:1706,% | 701 | Resistive ground current in isol systems (Ins Real) Measurement 134 137 No 9 15 CFC CD DD |  |
| RTU1:134:152¦M103,1.7,100.0,0:1706,% | 702 | Reactive ground current in isol systems (Ins) Measurement 134 137 No 9 16 CFC CD DD |  |